## HTM Records
name | buildingName | level | area | existingInstallType | existingCondition | repairReplace | status | lDform1Fitter | lDpenServ | repairType | access | cwDate | dateNext | role | other | completeBy | detailsRepairReplacement | comments | detailsRepairsReplacementsCarriedOut | existingFireStoppingNumber | newFireStoppingNumber | productManufacturersDetails | otherRelevantInformation
Pfp-001 | 1 Richmond Way | Basement | Storage | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | Slab Penetration Mechanical Pipework | Full Replacement | Yes | 2020-03-16T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | Storage |  | Fit a patress to ceiling with screws around the water pipe, wrap water pipe with protcta wrap, screw in to ceiling with screws and washers making sure if secure fit. Tape off and coat up all edges | Minor works | Fit a patress seal to the ceiling securing with screws and washers, wrapped the water pipe with protecta wrap and used protecta mastic to seal all gaps, covered all edges as well | No label | Pfp-001 |  | Work complete
Pfp-002 | 1 Richmond Way | Basement | Storage | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | Wall Penetration Other | Full Replacement | Yes | 2020-03-16T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | Storage |  | Fit protecta batt around edges of seal closing off all gaps to make the seal compliant | Minor works | Friction fit protecta ball around open edges of plasterboard, sealed all gaps making seal compliant | No label | Pfp-002 |  | Work complete
Pfp-003 | 1 Richmond Way | Basement | Storage | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | Slab Penetration Mechanical Pipework | Full Replacement | Yes | 2020-03-16T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | Storage |  | Fit a patress to the wall with screws around the water pipe, wrap water pipe with protcta wrap, screw in to the wall with screws and washers making sure if secure fit. Tape off and coat up all edges | Minor works | Fit a patress seal to the wall securing with screws and washers, wrapped the water pipe with protecta wrap and used protecta mastic to seal all gaps, covered all edges as well | No label | Pfp-003 |  | Work complete
Pfp-004 | 1 Richmond Way | Ground Floor | BOH | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | Ionut Rusu (Hamarks) | Wall Penetration Multiple Cable No Containment | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | Ground floor riser |  | 12 x holes with cables need closing with mastic | Minor works | Filled in gaps around cables with protecta mastic making the seals compliant | No label | Pfp-004 |  | Work complete
Pfp-005 | 1 Richmond Way | Ground Floor | BOH | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | Ionut Rusu (Hamarks) | Wall Penetration Ductwork | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | Ground floor riser |  | Remove foam, put envirograff duct wrap around duct then firestop hole as required | Minor works | Removed plasterboard, removed some foam, fitted envirograff wrap around duct securing tightly. Fire stopped around duct with protecta batt and mastic Leaving no gaps making the seal compliant | No label | Pfp-005 |  | Work complete
Pfp-006 | 1 Richmond Way | Ground Floor | BOH | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | Ionut Rusu (Hamarks) | Wall Penetration Ductwork | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | Ground floor riser |  | Remove foam, put envirograff duct wrap around duct then firestop hole as required | Minor works | Removed some foam, fitted envirograff wrap around duct securing tightly. Fire stopped around duct with protecta batt and mastic Leaving no gaps making the seal compliant | No label | Pfp-006 |  | Work complete
Pfp-007 | 1 Richmond Way | Ground Floor | BOH | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | Ionut Rusu (Hamarks) | No Service Penetration or Clear Void | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | Ground floor riser |  | Friction fit batt over exposed beam | Minor works | Friction fitted protecta batt inside the brickwork covering the exposed steel work, sealed off all gaps making the seal compliant | No label | Pfp-007 |  | Work complete
Pfp-008 | 1 Richmond Way | Ground Floor | Stairs | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | No Service Penetration or Clear Void | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | Ground floor riser |  | Build a bulk head to encase the exposed wooden staircase, double board with fire line plasterboard | Minor works | Built frame and fixed securely in place, overboarded with fire line plasterboard double layer and mastic over Joints | No label | Pfp-008 |  | Work complete
Pfp-009 | 1 Richmond Way | Ground Floor | BOH | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | No Service Penetration or Clear Void | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2020-03-25T00:00:00.0000000Z |  | Ground floor riser |  | Remove all old plasterboard then remove all old chipboard, insulate with approved acoustic insulation then overboard with 15mm fireline plasterboard and mastic over any gaps | Minor works | Removed the old plasterboard and chipboard,used appropriate insulation then overboarded with 15mm fireline plasterboard double layer, fixed to original stud work and filled in gaps with protecta mastic | No label | Pfp-009 |  | Work complete
Pfp-010 | 1 Richmond Way | Ground Floor | BOH | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | No Service Penetration or Clear Void | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | Ground floor riser |  | Remove all old plasterboard then remove all old chipboard, insulate with approved acoustic insulation then overboard with 15mm fireline plasterboard and mastic over any gaps | Minor works | Remove all old plasterboard then remove all old chipboard, insulated with approved acoustic insulation then overboard with 15mm fireline plasterboard double layer and mastic over any gaps | No label | Pfp-010 |  | Work complete
Pfp-011 | 1 Richmond Way | Ground Floor | BOH | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | Wall Penetration Ductwork | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | Ground floor riser |  | Plasterboard needs to be completed to seal the room and cover exposed steel columns,and ventilation ductwork needs to be fire stopped | Very tight access | Insulated wall with approved acoustic insulation then overboarded with 15mm fireline plasterboard double layer, fire stopped in corner where air ducts are passing through the wall.wrapped 2 ducts with protecta endless wraps and closed of void with protecta batt and mastic leaving no gaps making the seal compliant | No label | Pfp-011 |  | Work complete
Pfp-012 | 1 Richmond Way | Ground Floor | BOH | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | No Service Penetration or Clear Void | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | Ground floor riser |  | Pull up floorboards remove any insulation if any and fire stop the floor where possible with intudeck 70mm batt and mastic | Very tight access | Removed floorboards with skill saw, removed insulation where needed and friction fitted between joists intruder batt and mastic making sure of a tight fit, filled in all gaps with approved mastic and replaced back the insulation and then replaced the floorboards | No label | Pfp-012 |  | Work complete
Pfp-013 | 1 Richmond Way | Ground Floor | BOH | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | No Service Penetration or Clear Void | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | Ground floor riser |  | Fire stop edge of plasterboard where it meets the wall | Minor works | Friction tion fitted protecta batt inside the edge of the plasterboard leaving no gaps leaving the seal compliant | No label | Pfp-013 |  | Work complete
Pfp-014 | 1 Richmond Way | Ground Floor | BOH | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | Wall Penetration Multiple Cable No Containment | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | Ground floor riser |  | Fit a patress seal around the bunch of cables | Minor works | Fit a patress to wall with screws and washers, covered all edges with protecta mastic | No label | Pfp-014 |  | Work complete
Pfp-015 | 1 Richmond Way | First Floor | Stairs | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | Wall Penetration Ductwork | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | 1st floor riser |  | Remove foam, put envirograff duct wrap around duct then firestop hole as required | Very tight access | Removed all foam, fitted envirograff wrap around duct securing tightly. Fire stopped around duct with protecta batt and mastic Leaving no gaps making the seal compliant | No label | Pfp-015 |  | Work complete
Pfp-016 | 1 Richmond Way | First Floor | Stairs | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | Wall Penetration Ductwork | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | 1st floor riser |  | Remove foam, put envirograff duct wrap around duct then firestop hole as required | Very tight access | Removed all foam, fitted envirograff wrap around duct securing tightly. Fire stopped around duct with protecta batt and mastic Leaving no gaps making the seal compliant | No label | Pfp-016 |  | Work complete
Pfp-017 | 1 Richmond Way | First Floor | Stairs | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | Wall Penetration Ductwork | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | 1st floor riser |  | Remove foam, put envirograff duct wrap around duct then firestop hole as required | Very tight access | Removed all foam, fitted envirograff wrap around duct securing tightly. Fire stopped around duct with protecta batt and mastic Leaving no gaps making the seal compliant | No label | Pfp-017 |  | Work complete
Pfp-018 | 1 Richmond Way | First Floor | Stairs | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | Wall Penetration Ductwork | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | 1st floor riser |  | Remove foam, put envirograff duct wrap around duct then firestop hole as required | Very tight access | Removed all foam, fitted envirograff wrap around duct securing tightly. Fire stopped around duct with protecta batt and mastic Leaving no gaps making the seal compliant | No label | Pfp-018 |  | Work complete
Pfp-019 | 1 Richmond Way | First Floor | Stairs | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | Wall Penetration Ductwork | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | 1st floor riser |  | Patress over the head of the wall to close all gaps and seal around spiral air duct | Minor works | Fit a patress seal to the wall securing with screws and washers, used protecta mastic where needed to seal all gaps, covered all edges as well | No label | Pfp-019 |  | Work complete
Pfp-020 | 1 Richmond Way | First Floor | Stairs | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | Wall Penetration Ductwork | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | 1st floor riser |  | Patress over the head of the wall to close all gaps and seal around air ducts | Minor works | Fit a patress seal to the wall securing with screws and washers,and used hp protecta mastic where needed to seal all gaps, covered all edges as well | No label | Pfp-020 |  | Work complete
Pfp-021 | 1 Richmond Way | First Floor | Stairs | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | Wall Penetration Ductwork | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | 1st floor riser |  | Patress over the head of the wall to close all gaps and seal around air ducts | Minor works | Fit a patress seal to the wall securing with screws and washers, wrapped the air con pipes with protecta wrap and used protecta mastic and hp to seal all gaps, covered all edges as well | No label | Pfp-021 |  | Work complete
Pfp-022 | 1 Richmond Way | First Floor | Stairs | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | No Service Penetration or Clear Void | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | 1st floor riser |  | Remove all old plasterboard then remove all old chipboard, insulate with approved acoustic insulation then overboard with 15mm fireline plasterboard and mastic over any gaps | Minor works | Remove all old plasterboard then remove all old chipboard, insulated with approved acoustic insulation then overboard with 15mm fireline plasterboard double layer and mastic over any gaps | No label | Pfp-022 |  | Work complete
Pfp-023 | 1 Richmond Way | First Floor | Stairs | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | No Service Penetration or Clear Void | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | 1st floor riser |  | Remove all old plasterboard then remove all old chipboard, insulate with approved acoustic insulation then overboard with 15mm fireline plasterboard and mastic over any gaps | Minor works | Remove all old plasterboard then remove all old chipboard, insulated with approved acoustic insulation then overboard with 15mm fireline plasterboard double layer and mastic over any gaps | No label | Pfp-023 |  | Work complete
Pfp-024 | 1 Richmond Way | First Floor | Stairs | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | No Service Penetration or Clear Void | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | 1st floor riser |  | Pull up floorboards remove any insulation if any and fire stop the floor where possible with intudeck 70mm batt and mastic | Minor works | Removed floorboards with skill saw, removed insulation where needed and friction fitted between joists intruder batt and mastic making sure of a tight fit, filled in all gaps with approved mastic and replaced back the insulation and then replaced the floorboards | No label | Pfp-024 |  | Work complete
Pfp-025 | 1 Richmond Way | First Floor | Stairs | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | Slab Penetration Mechanical Pipework | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | 1st floor riser |  | Fit a patress to the soffit with screws and washers sealing around the 4 water pipes | Minor works | Fit a patress seal to the soffit securing with screws and washers,and used protecta mastic where needed to seal all gaps, covered all edges as well | No label | Pfp-025 |  | Work complete
Pfp-026 | 1 Richmond Way | Second Floor | Stairs | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | Wall Penetration Ductwork | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | 2nd floor riser |  | Fit a patress to the head of the wall seal around air con ducts | Minor works | Fit a patress seal to the head of the wall securing with screws and washers,and used protecta mastic where needed to seal all gaps, covered all edges as well | No label | Pfp-026 |  | Work complete
Pfp-027 | 1 Richmond Way | Second Floor | Stairs | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | Wall Penetration Ductwork | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | 2nd floor riser |  | Fire stop around air con ducts with hp mastic | Minor works | Filled in gaps around cables and air con ducts using protecta hp mastic making the seal compliant | No label | Pfp-027 |  | Work completed but very restricted access
Pfp-028 | 1 Richmond Way | Second Floor | Stairs | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | Wall Penetration Ductwork | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | 2nd floor riser |  | Remove foam, put envirograff duct wrap around duct then firestop hole as required | Minor works | Removed all foam, fitted envirograff wrap around duct securing tightly. Fire stopped around duct with protecta batt and mastic Leaving no gaps making the seal compliant | No label | Pfp-028 |  | Work complete
Pfp-029 | 1 Richmond Way | Second Floor | Stairs | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | Wall Penetration Ductwork | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | 2nd floor riser |  | Remove foam, put envirograff duct wrap around duct then firestop hole as required | Minor works | Removed all foam, fitted envirograff wrap around duct securing tightly. Fire stopped around duct with protecta batt and mastic Leaving no gaps making the seal compliant | No label | Pfp-029 |  | Work complete
Pfp-030 | 1 Richmond Way | Second Floor | Stairs | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | Wall Penetration Ductwork | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | 2nd floor riser |  | Remove foam, put envirograff duct wrap around duct then firestop hole as required | Minor works | Removed all foam, fitted envirograff wrap around duct securing tightly. Fire stopped around duct with protecta batt and mastic Leaving no gaps making the seal compliant | No label | Pfp-030 |  | Work complete
Pfp-031 | 1 Richmond Way | Second Floor | Stairs | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | Wall Penetration Ductwork | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | 2nd floor riser |  | Remove foam, put envirograff duct wrap around duct then firestop hole as required | Minor works | Removed all foam, fitted envirograff wrap around duct securing tightly. Fire stopped around duct with protecta batt and mastic Leaving no gaps making the seal compliant | No label | Pfp-031 |  | Work complete
Pfp-032 | 1 Richmond Way | Second Floor | Stairs | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | Wall Penetration Ductwork | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | 2nd floor riser |  | Fire stop head of wall sealing around all air con ducts and pipe work | Difficult acess | Filled in gaps at head of wall with protecta batt and mastic, sealed around air con ducts with protecta hp mastic making the seal compliant | No label | Pfp-032 |  | Work completed but very restricted access
Pfp-033 | 1 Richmond Way | Second Floor | Stairs | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | Slab Penetration Mechanical Pipework | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | 2nd floor riser |  | Fire stop around pipes | Minor works | Used protecta mastic to seal around pies leaving no gaps leaving the seal compliant | No label | Pfp-033 |  | Work complete
Pfp-034 | 1 Richmond Way | Second Floor | Stairs | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | No Service Penetration or Clear Void | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | 2nd floor riser |  | Apply a mastic bead to the head of the wall | Minor works | Applies a mastic bead to joint at the head of the wall | No label | Pfp-034 |  | Work complete
Pfp-035 | 1 Richmond Way | Second Floor | Stairs | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | Wall Penetration Multiple Cable No Containment | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | 2nd floor riser |  | Fire stop cable trays and pipes coming through the slab | Very tight access | Friction fitted protecta batt inside the joists, wrapped the plastic pipe and air con pipes with protecta wrap, sealed off all gaps making the seal compliant | No label | Pfp-035 |  | Work completed but very restricted access
Pfp-036 | 1 Richmond Way | Second Floor | Stairs | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | No Service Penetration or Clear Void | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | 2nd floor riser |  | Remove all old plasterboard then remove all old chipboard, insulate with approved acoustic insulation then overboard with 15mm fireline plasterboard and mastic over any gaps | Minor works | Remove all old plasterboard then remove all old chipboard, insulated with approved acoustic insulation then overboard with 15mm fireline plasterboard double layer and mastic over any gaps | No label | Pfp-036 |  | Work complete
Pfp-037 | 1 Richmond Way | Third Floor | Stairs | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | Wall Penetration Ductwork | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | 3rd floor riser |  | Remove foam, put envirograff duct wrap around duct then firestop hole as required | Very tight access | Removed all foam, fitted envirograff wrap around duct securing tightly. Fire stopped around duct with protecta batt and mastic Leaving no gaps making the seal compliant | No label | Pfp-037 |  | Work completed but very restricted access
Pfp-038 | 1 Richmond Way | Third Floor | Stairs | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | Slab Penetration Multiple Cable No Containment | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | 3rd floor riser |  | Fit a patress to the soffit with screws and washers sealing the length of head of wall making sure to seal around all pipes and cables | Very tight access | Fit a patress seal to the soffit running along the length of the head of wall. Sealed all cables and pipes | No label | Pfp-038 |  | Work completed but very restricted access
Pfp-039 | 1 Richmond Way | Third Floor | Stairs | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | Wall Penetration Ductwork | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | 3rd floor riser |  | Remove foam, put envirograff duct wrap around duct then firestop hole as required | Very tight access | Removed all foam, fitted envirograff wrap around duct securing tightly. Fire stopped around duct with protecta batt and mastic Leaving no gaps making the seal compliant | No label | Pfp-039 |  | Work completed but very restricted access
Pfp-040 | 1 Richmond Way | Third Floor | Stairs | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | Wall Penetration Ductwork | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | 3rd floor riser |  | Remove foam, put envirograff duct wrap around duct then firestop hole as required | Very tight access | Removed all foam, fitted envirograff wrap around duct securing tightly. Fire stopped around duct with protecta batt and mastic Leaving no gaps making the seal compliant | No label | Pfp-040 |  | Work completed but very restricted access
Pfp-041 | 1 Richmond Way | Third Floor | Stairs | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | Wall Penetration Ductwork | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | 3rd floor riser |  | Remove foam, put envirograff duct wrap around duct then firestop hole as required | Very tight access | Removed all foam, fitted envirograff wrap around duct securing tightly. Fire stopped around duct with protecta batt and mastic Leaving no gaps making the seal compliant | No label | Pfp-041 |  | Work complete
Pfp-042 | 1 Richmond Way | Third Floor | Stairs | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | Wall Penetration Ductwork | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | 3rd floor riser |  | Remove foam and fire stop around duct with protecta batt and mastic | Very tight access | Remove all foam then fire stop with protecta batt and mastic | No label | Pfp-042 |  | Work complete
Pfp-043 | 1 Richmond Way | Third Floor | Stairs | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | No Service Penetration or Clear Void | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | 3rd floor riser |  | Remove all old plasterboard then remove all old chipboard, insulate with approved acoustic insulation then overboard with 15mm fireline plasterboard and mastic over any gaps | Very tight access | Remove all old plasterboard then remove all old chipboard, insulated with approved acoustic insulation then overboard with 15mm fireline plasterboard double layer and mastic over any gaps | No label | Pfp-043 |  | Work complete
Pfp-044 | 1 Richmond Way | Third Floor | Stairs | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | No Service Penetration or Clear Void | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | 3rd floor riser |  | Remove all old plasterboard then remove all old chipboard, insulate with approved acoustic insulation then overboard with 15mm fireline plasterboard and mastic over any gaps | Very tight access | Remove all old plasterboard then remove all old chipboard, insulated with approved acoustic insulation then overboard with 15mm fireline plasterboard double layer and mastic over any gaps | No label | Pfp-044 |  | Work complete
Pfp-045 | 1 Richmond Way | Third Floor | Stairs | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | Wall Penetration Mechanical Pipework | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | 3rd floor riser |  | Fit a patress to the soffit with screws and washers sealing around the the cables and aircon pipes | Very tight access | Fit a patress seal to the soffit securing with screws and washers,and used protecta mastic where needed to seal all gaps, covered all edges as well wrapped the air on pipes in protecta wrap and used hp in the gaps. | No label | Pfp-045 |  | Work complete
Pfp-046 | 1 Richmond Way | Third Floor | Stairs | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | Wall Penetration Mechanical Pipework | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | 3rd floor riser |  | Fit a patress to the soffit with screws and washers sealing around the the water pipes | Very tight access | Fit a patress seal to the soffit securing with screws and washers,and used protecta mastic where needed to seal all gaps, covered all edges as well | No label | Pfp-046 |  | Work complete
Pfp-047 | 1 Richmond Way | Third Floor | Stairs | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | Wall Penetration Mechanical Pipework | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | 3rd floor riser |  | Fit a patress to the wall with screws and washers sealing around the the cables and aircon pipes | Very tight access | Fit a patress seal to the head of the wall securing with screws and washers,and used protecta mastic where needed to seal all gaps, covered all edges as well used hp mastic around air con ducts | No label | Pfp-047 |  | Work completed but very restricted access
Pfp-048 | 1 Richmond Way | Third Floor | Stairs | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | No Service Penetration or Clear Void | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-05-31T23:00:00.0000000Z |  | 3rd floor riser |  | Fit a patress to the head of the wall seal around air con ducts | Very tight access | Fit a patress seal to the head of the wall securing with screws and washers,and used protecta mastic where needed to seal all gaps, covered all edges as well used hp mastic around air con ducts | No label | Pfp-048 |  | Work complete
Pfp-049 | 1 Richmond Way | Third Floor | Stairs | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | Multi Services Mechanical/Electrical | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | 3rd floor riser |  | Fire stop cable trays and pipes coming through the slab | Very tight access | Friction fitted protecta batt inside the joists, wrapped the plastic pipe and air con pipes with protecta wrap, sealed off all gaps making the seal compliant | No label | Pfp-049 |  | Work completed but very restricted access
Pfp-050 | 1 Richmond Way | Ground Floor | Refuse | No Existing Installation | Compliant to Trident Spec | Repaired | Inspection Completed - No Works Required | David Jonesb (Hamarks) | Slab Penetration Mechanical Pipework | Full Replacement | Yes | 2020-03-18T00:00:00.0000000Z | 2021-01-01T00:00:00.0000000Z |  | Bin store |  | Wrap svp then fit a patress around it | Minor works | Wrapped the pipe in protecta wrap then fit a patress around it securing to the ceiling with screws and washers coating up all edges making the seal compliant | No label | Pfp-050 |  | Work complete